1.0	Purpose

To ensure that Field employees, Field Supervisors, and Safety representatives understand the general use of scaffolding as it applies to EM&FS service work and projects.

2.0	Scope

Field personnel shall know how to safely use scaffolding as well as identify where scaffolding can be used, where it is not to be used, how high self erected scaffolding is allowed, and the type of scaffolding supported by this SWP.

3.0	Responsibility

The responsibility for seeing that this safe work practice is followed is binding upon all employees.  All employees shall be instructed in the safety significance of this program. Each new or transferred affected employee shall be instructed in the purpose and use of this program. The Responsible Manager is accountable for implementing and enforcing this procedure.

·

The Safety Director is responsible for monitoring compliance with this procedure and keep a written record of the training for each employee.

·

The Employee is responsible for working within their qualifications and following EMCOR Mechanical and Facilities Services Safe Work Practices (SWP). Failure to follow this safe work practice may lead to disciplinary action up to and including termination.

- Special Definitions

Competent Person- By way of training and/or experience, a competent person is knowledgeable of applicable standards, is capable of identifying workplace hazards relating to the specific operation, and has the authority to correct them. A Competent Person will provide training to each employee who performs work while on a scaffold to recognize the hazards associated with the type of scaffolding being used and to understand the procedures to control or minimize those hazards.

Qualified Person- Possesses a recognized degree, certificate, or professional standing, with extensive knowledge, training and experience; and can resolve problems related to the work or project. A qualified person must do adequate preplanning to ensure the safe erection and use of the scaffold.

5.0	Requirements

EMCOR Mechanical and Facilities Services employees self erecting scaffolding must be properly trained and scaffolding should not exceed two tier high. Erecting scaffolding more than two tiers high must be reviewed and approved by your company safety director and under the direction of a competent, qualified person. In addition, erected scaffolding must also comply with any state requirements that are more stringent than OSHA or other regulatory requirements. Normally, scaffolding exceeding 2 tiers should be sub contracted to a qualified contractor.

Retraining is required in at least the following situations: Where changes at the 	worksite present a hazard about which an employee has not 	been previously 	trained; or where changes in the types of scaffolds, fall protection, fall object 	protection, o other 	equipment present a hazard about which an employee has not 	been previously trained; or where inadequacies in an affected employee’s work 	involving scaffolds indicate that the employee has not retained the requisite 	proficiency.

6.0	 Procedure

- Scaffolds shall be erected on sound, rigid footing, capable of carrying the maximum intended load without settling or displacement and be located no more than 14 inches from the area where work is being performed.

- Scaffolds and their components shall be capable of supporting, without failure, at least 4 times the intended load.

- Guardrails and toeboards shall be installed on all open sides and ends of platforms more than 10 feet high above the ground or floor level.

- Scaffolds 4 feet to 10 feet in height, having minimum dimensions in either direction of less than 45 inches, shall have standard guardrails installed on all open sides and ends of platform.

- There shall be screen with a maximum ½ inch openings between the toeboard and the guardrail, where workers are required to work or pass under the scaffold.

- All planking shall be scaffold grade or equivalent as recognized by grading rules for species of wood used.

- The maximum permissible spans for 2”x10” or wider planks are indicated in the following table.

| Working Load (lbs. per Sq. ft.) | 25 | 50 | 75 |
| --- | --- | --- | --- |
| Permissible Span (ft.) | 10 | 8 | 6 |

- Scaffold planking shall extend over end supports not less than 6 inches nor more than 12 inches

- An access ladder or equivalent safe access shall be provided

- Platform shall be 100% planked with no more than 1 inch gaps for full width of scaffold except for necessary entrance opening. Platforms shall be secured in place.

- Guardrails made of lumber, not less than 2”x4”, approximately 42” in height, with a midrail of 1”x6” or equivalent.

- Guardrails plus toeboards shall be installed on all scaffolds over 10 feet in height.

- Toeboards shall be a minimum of 4” in height.

- Scaffold Tagging:  A Red Tag indicates the scaffolding is not permitted to be in use. A Green Tag indicates that the scaffolding is acceptable for use. All scaffolding shall have a green tag before being used. A Yellow Tag indicates fall protection is required. All yellow tags must be accompanied by a green tag. All tags shall be hung at the access point. No Tag is the same as a red tag.

- Lockout/Tagout: All sources of energy which create a hazard to the scaffold user shall be isolated, or locked out. Work on scaffolding (Especially Mobile Scaffold) shall not be permitted within ten feet of electric lines unless the lines have been locked out or protected. Mobile equipment shall be routed away from the scaffolding.

- Mobile Scaffold: See LOTO. Employees are not permitted to ride scaffolding while it is being moved. When scaffold is moved an observer shall be present to watch for overhead hazards, such as electric lines.

- Securing Planks: All planks shall be secured by bolting, nailing, wiring down or overlapping each other by not less than 12 inches. If planks are not secured properly they shall extend over the edge of the scaffolding by 6 to 12 inches.

- Toeboards: A four inch barrier shall be secured along the long side and ends of all work platforms above four feet to guard the falling of loose tools, materials and other objects.

- Guardrails: A toprail and a midrail shall be secured to uprights and erected along the exposed sides and ends of the platform. Both the toprail and the midrail shall be able to support 200 pounds of force.

- Area below scaffolding: The area below the scaffolding shall, at a minimum, be roped off with red or yellow tape and have signs posted that warn of overhead work. Safety lookouts may be required.

- Conditions which weaken scaffolding: If any part of the scaffold is cut, bent, burned, missing or subjected to unusual strain, the scaffolding shall not be used until the affected sections are replaced.

- Scaffolding Inspection Checklist: Regardless of who erects the scaffolding, the “Scaffolding Inspection Checklist” must be completed by at least one of the affected employees prior to use.

6.0	Associated and Related Documents

- SWP50.EMFSScaffolding Inspection Checklist